## Sayfa1
inputs
core features
specifications |  |  |  | type | squere-core |  |  | design values
power(VA) | 500000 |  |  | lamination type | no lamination |  |  | N1(in) | 1200
Vin(V) | 34500 |  |  | material | steel |  |  | N2(out) | 869.5652
Vout(V) | 25000 |  |  | B(T) | 1.2 | write by using B-H curve
Freq(Hz) | 50 |  |  | H(At/m) | 1000
temp(C) | 40 |  |  | Core loss(W/kg),1T | 0.95 | *Bop^2, laminasyona göre değişir |  | N1/N2 | 1.38
J(A/mm2) | 3 |  |  | material density(g/cm^3) | 7.85
Ku(fill factor) | 0.3 |  |  | material cost ($/kg) | 3
power factor | 1 |  |  | cable features
|  |  |  | material | copper |  |  |  | m^2 | mm^2
Iin | 14.4928 |  |  | resistivity(ohm/m) | 1.68e-08 |  |  | window area | 0.038647 | 38647.343
Iout | 20 |  |  | cable cost in($/m) | 1
|  |  |  | cable cost out($/m) | 1 |  |  | y1(G),y2(F) | 0.19659 | 196.5893 | !! İf it is square this value can be write input at left
| mm^2 | m^2 |  | Core permiability | 0.0012
cable cross sec(in) | 4.8309 | 4.8309e-06 |  | Core relative perm(ur) | 955.414 |  |  | window sizes(square,inner) | m | mm
cable cross sec(out) | 6.6667 | 6.6667e-06 | [5 empty] | y1(G) | 0.196 | 196 | sarım yapılan kenar
[5 empty] | m^2 | mm^2
| mm | mm |  | req cross sec area | 0.10792 | 107920.4204 |  | y2(F) | 0.19718 | 197.1803
cable radius(in) | 1.24 | 1.2404 | [5 empty] | kare ise bu ikisi eşit
cable radius(out) | 1.457 | 1.4571 |  |  | m | mm
copper yarıcapları akım density sabit alınarak heaplanmıştır,duruma göre ayarlanabilir, sağdaki densityden hesaplanan değer inputa yazılır |  |  |  | x1(D),x2(E,R) | 0.32851 | 328.5124 | !! İf it is square this value can be write input at left
|  |  |  | cross section sizes | m | mm
|  |  |  | x1(D) | 0.36 | 360 |  |  | m
[8 empty] | B | 0.79556
| mm |  |  | x2(E,R) | 0.29978 | 299.7789 |  | A | 0.79674
Mean Length Turn radius | 213.5513 |  |  | kare ise bu ikisi eşit |  |  |  | taking reference from dimension figure
| mm | m
cable lenght(in) | 1609322.5833 | 1609.3226 |  |  | g | kg
cable lenght(out) | 1166175.785 | 1166.1758 |  | core mass | 1682046.5868 | 1682.0466 |  |  | m
[8 empty] | Core Effective Length | 1.9855
Copper resistance(in) R1(ohm) | 5.5966
Copper resistance(out) R2(ohm) | 2.9392 | [6 empty] | Core Reluctance | 15331.331
Copper loss(W),in | 1175.5052
Copper loss(W),out | 1175.6676
Total Copper loss(W) | 2351.1728 |  |  | core loss(W) | 2301.0397
[8 empty] | inner Inductance, L1(H) | 93.9253
[8 empty] | outer inductance,L2(H) | 49.3202
[8 empty] | mutual inductance(H) | 68.0618
|  | efficiency | 0.99078 |  | core cost | 5046.1398
[5 empty] | inner cable cost | 1609.3226
[5 empty] | outer cable cost | 1166.1758
[5 empty] | Total cost | 7821.6381
next figure is using only figure dimensions.